MEMORANDUM

To:			Brian Gray [TECHNICAL SAFETY BC]

From:			Ash Parmar/Laura Sisson, P.Eng.

Date:			April 27, 2026

Re:			Refrigerant System Code Compliance Review

Revision: 		Rev1

Project Number:	2171368

# Purpose

## This memorandum summarizes the review completed for the refrigeration system serving Air Handling Unit AHU-04 located on MR-09 (Mechanical Room 09) serving the morgue. The review was undertaken in response to questions raised by the Authority Having Jurisdiction regarding the use of an A2L refrigerant and the requirements of CSA B52:2023 Mechanical Refrigeration Code.

The intent of this document is to:

#### describe the refrigeration system configuration

#### confirm the applicable code provisions

#### document the effective dispersal volume used for evaluation

#### compare the installed refrigerant charge with the allowable charge limit

#### outline provisions for refrigerant detection in accordance with CSA B52

#### Response to TSBC inspection report number: BPVIN-5091852-2026 dated 10-April-2026.

Project: Royal Inland Hospital Pharmacy Booster Fan System
To: Interior Health
Attention: Ron Potts
From: H.H. Angus & Associates Limited
Date: [Insert Date]
Subject: Pharmacy HVAC System Performance Review, Risk Assessment, and Recommended Path Forward

# Purpose

## This memorandum has been prepared in response to Interior Health’s request for a technical assessment of the current performance of the Pharmacy HVAC system, including the booster fan installation and associated Galardi Tower air handling units (AHU 4, 5, and 6).

#### This document provides:

#### Clarification of system configuration and airflow paths

#### Review of current system performance

#### Comparison to previous observations and design intent

#### Technical assessment of system behavior

#### Updated risk and redundancy assessment

#### Recommended actions and next steps

- 2. System Configuration and Airflow Paths

The Pharmacy supply system consists of two interconnected airflow segments that must be considered together to understand overall system performance.

- 2.1 Base Building AHU Supply Path

Supply air originates from AHU 4, 5, and 6 and follows an extended distribution path:

- Air is supplied from AHU 4, 5, and 6

- Routed through base building ductwork

- Transitions to exterior duct runs

- Travels across roof level duct systems with multiple fittings and transitions

- Arrives at the booster fan inlet location

This portion of the system includes long duct runs and multiple transitions, contributing to overall system resistance.

- 2.2 Booster Fan System

At roof level, booster fans provide supplemental airflow energy:

- Air enters the booster fan plenum

- Booster fans increase airflow energy

- Air is discharged back into ductwork

- Duct drops into the Pharmacy area

- Air is distributed to Pharmacy spaces and adjacent zones through downstream duct branches

- 2.3 System Interaction

System performance depends on:

- Upstream airflow delivery from AHUs

- Losses through exterior duct routing

- Booster fan performance

- Downstream distribution efficiency

Any inefficiency within these segments impacts overall system performance.

- 3. Redundancy Configuration

Redundancy for the Pharmacy system is provided through two mechanisms:

- 3.1 Base Building AHU Redundancy

The system includes connection to AHU 1, 2, and 3 via ductwork equipped with isolation dampers.

Under contingency conditions:

- Isolation dampers may be opened

- AHU 1, 2, and 3 can supplement airflow to the Pharmacy system

This represents the primary redundancy strategy.

- 3.2 Booster Fan Redundancy

The booster fan system includes:

- Two parallel fans

- Intended operation under dual-fan conditions

- Partial capacity available under single-fan operation

Backdraft dampers are required to:

- Prevent reverse airflow

- Allow effective fan isolation

- Enable meaningful redundancy

- 4. Current Observed System Performance

Based on recent BAS observations:

- AHU 4, 5, and 6 operating at approximately 98 to 100 percent

- Booster fans operating at approximately 96 to 98 percent

- Pharmacy VAV dampers near fully open

- Backdraft dampers not yet installed

A key observed change is:

- Static pressure at AHU 4, 5, and 6 has decreased by approximately 150 Pa

This indicates that booster fans are providing measurable upstream relief.

- 5. Comparison to Previous Observations

- 5.1 Previous Condition (April 2024)

- High static pressure at AHUs

- Limited airflow delivery

- No booster fan support

- 5.2 Current Condition

Following booster fan installation:

- Static pressure has reduced

- Additional airflow energy has been introduced

- System capacity has increased

However:

- Downstream airflow demand remains unmet

- VAV dampers remain fully open

- System continues to operate near maximum capacity

- 6. System Performance Reconciliation

The current system behavior presents a critical observation:

- Static pressure has decreased

- Booster fans are operating at high capacity

- Downstream airflow demand remains unmet

This indicates that:

- The system is successfully generating airflow

- The booster fans are reducing upstream system resistance

- However, the additional airflow energy is not being effectively delivered to the Pharmacy spaces

Engineering Interpretation:

The system is not limited by fan capacity. It is limited by airflow transmission and delivery within the distribution system.

- 7. Technical Assessment

Based on current data, the most likely contributing factors are:

- 7.1 Airflow Distribution Loss

Potential contributors:

- Duct leakage

- Disconnected or unsealed duct sections

- Bypass airflow paths

- Reverse flow prior to damper installation

- 7.2 Elevated System Resistance

Potential contributors:

- HEPA filter pressure drop

- Extended duct routing and transitions

- Installation-related constraints

- 7.3 Control and Measurement Limitations

Potential contributors:

- Static pressure sensor location

- Booster fan control logic

- Flow measurement accuracy

- Interaction between AHUs and booster fans

- 8. Risk Assessment

- 8.1 Current Condition

The system is operating with minimal capacity margin.

Risks include:

- Loss of airflow under upset conditions

- Inability to maintain required pressure relationships

- Increased equipment wear

- 8.2 Redundancy

While redundancy exists:

- AHU 1, 2, and 3 can supplement airflow

- Booster fans provide local redundancy

Current performance indicates:

- Redundancy has not yet been validated under real conditions

- System behavior under failure scenarios remains unconfirmed

- 8.3 Backdraft Dampers

Installation of backdraft dampers is expected to:

- Prevent reverse airflow

- Improve system stability

- Support redundancy

- 9. Recommended Actions

- 9.1 Backdraft Damper Installation

- Complete installation

- Confirm proper orientation and operation

- 9.2 Airflow Verification

Perform targeted airflow measurements:

- Booster fan discharge

- Upstream and downstream duct sections

- Pharmacy VAV airflow

Objective:

- Confirm actual airflow delivery

- Identify location of losses

- 9.3 Duct System Verification and Correction

- Verify accessible duct sections

- Identify leakage, obstruction, or disconnection

- Implement corrections where identified

- 9.4 Control System Review

Confirm:

- Static pressure setpoints

- Sensor locations

- Booster fan control logic

- VAV calibration

- 9.5 System Validation Testing

Following corrective actions:

- Verify dual-fan operation

- Verify single-fan operation

- Confirm airflow delivery and pressure relationships

- 9.6 Key Immediate Action

Given the system is currently operating at near maximum capacity across all major components, corrective actions should prioritize restoring effective airflow delivery before considering any increase in system capacity.

- 10. Additional Information Required

To support ongoing evaluation, the following information is requested:

- Pharmacy certification report following HEPA replacement

- Filter pressure drop data

- BAS adjustments completed to date

- Confirmation of duct modifications or sealing

- Backdraft damper installation schedule

- 11. Conclusion

The system demonstrates:

- Increased airflow energy from booster fans

- Reduced upstream static pressure

- Continued inability to satisfy downstream airflow demand

This confirms that:

The limiting factor is not airflow generation, but airflow delivery.

The recommended approach focuses on:

- Verifying airflow delivery

- Identifying distribution losses

- Stabilizing system operation

- Confirming redundancy performance

If you want to take this one level higher, I can:

- add an executive summary for Ron

- align wording exactly with HHA letter templates

- or tailor tone more aggressive depending on how political this is about to get